## DB-B1
DB-B1 · SLD Component Extraction · DB-B1.dwg
Groups: 11 ¦ Total units: 47
# | Category | Label | Poles | Amps | Curve | B.C. | Sensitivity | SPD Type | Cable mm² | Load / Circuit | Qty | Terminal? | Conf. | Source | AI Notes
1 | SWITCH | ISOL.S. | 4P | 40A | - | - | - | - | 10.0 | MAIN INCOMER | 1 | - | 100% | BOTH | Incomer identified from 'SW' block and 4x40A text. Feeder cable 4Cx10mm2 identified in drawing header.
2 | METER | DIGITAL POWER METER | 3P | - | - | - | - | - | - | Panel Metering | 1 | - | 100% | BOTH | -
3 | METER | CT | 3P | - | - | - | - | - | - | Metering CTs | 3 | - | 90% | IMAGE_ONLY | Mandatory CT inclusion for 3-phase panel.
4 | PILOT_LAMP | Indicator Lamp | R/Y/B | - | - | - | - | - | - | Phase Indication | 3 | - | 100% | BOTH | 3 lamps (Red, Green, Blue) as per block counts.
5 | FUSE_HOLDER | Fuse gG | 3P | 32A | - | - | - | - | - | SPD protection | 1 | - | 100% | BOTH | -
6 | SPD | TYPE 2 / CLASS C | 4P | - | - | 20kA | - | Type 2, Up<=1.2KV | - | Surge Protection | 1 | - | 100% | BOTH | -
7 | RCCB | ISOL.S.+RCD | 4P | 16A | - | - | 300mA | - | - | Lighting Sections | 2 | - | 100% | BOTH | Sourced from blocks '4x10 300mA' and clusters 011, 210.
8 | RCCB | ISOL.S.+RCD | 4P | 25A | - | - | 30mA | - | - | Socket Sections | 2 | - | 100% | BOTH | Sourced from blocks '4x25 300mA' (mismatched name) and clusters 046, 219.
9 | MCB | IC60H | 1P+N | 10A | C | 6kA | - | - | 2.5 | L1, L2, L3, L4, L5, L6, L7, L8, L9, L10, L11, L12, L13, L14, Spare, Spare | 16 | ✓ | 100% | BOTH | B.C. from global note. Qty from block '2x10' count.
10 | MCB | IC60H | 1P+N | 16A | C | 6kA | - | - | 2.5 | Sockets - Corridor/Coldroom/Storage, R2, R3, R4, R5, R6, R7, Spare (St-By), Socket - Pool Bathroom, R14, R15, Sockets - Spare, Sockets - Parking | 13 | ✓ | 90% | BOTH | B.C. from global note. Sub-group of '2X16' block count.
11 | MCB | IC60H | 1P+N | 20A | C | 6kA | - | - | 4.0 | Socket - Technical Room, Socket - Kitchen Appliance, Socket - Kitchen Appliance, Socket - Kitchen Appliance | 4 | ✓ | 90% | BOTH | Identified from 2x20 text clusters (214, 222, 234) and 3x4 cable size.
DB-B1 · Terminal Block Schedule
Types: 2 ¦ Total terminals: 37
# | Terminal Type | Description | Max mm² | Qty | Circuits
1 | Terminal 10mm² | Phoenix Contact PT 10 feed-through | 10 | 4 | [INCOMER] MAIN INCOMER 40A 4P @10.0mm² (4 terminals)
2 | Terminal 2x4mm² | Phoenix Contact PT 4 feed-through | 4 | 33 | L1, L2, L3, L4, L5, L6, L7, L8, L9, L10, L11, L12, L13, L14, Spare, Spare 10A @2.5mm² ¦ Sockets - Corridor/Coldroom/Storage, R2, R3, R4, R5, R6, R7, Spare (St-By), Socket - Pool Bathroom, R14, R15, Sockets - Spare, Sockets - Parking 16A @2.5mm² ¦ Socket - Technical Room, Socket - Kitchen Appliance, Socket - Kitchen Appliance, Socket - Kitchen Appliance 20A @4.0mm²
|  |  | TOTAL | 37

## Drawing
DB-B1 · Drawing Render · DB-B1.dwg