## Components
SLD Component Extraction · xyz.dwg
Groups: 15 ¦ Total units: 38
# | Category | Label | Poles | Amps | Curve | B.C. | Sensitivity | SPD Type | Cable mm² | Load / Circuit | Qty | Terminal? | Conf. | Source | AI Notes
1 | MCCB | MCCB 100AF | 4P | 100A | C | 36kA | - | - | 35.0 | EDL-1 Input, EDL-2 Input | 2 | - | 100% | BOTH | Identified from text 'MCCB: AF=100A AT=100A' and '4x35mm2'. Feeds KWH meters.
2 | METER | KWH Meter | 3P | - | - | - | - | - | - | Utility Metering | 2 | - | 100% | DXF_ONLY | Text 'KWH-1', 'KWH-2'.
3 | OTHER | Phase Failure Relay | - | - | - | - | - | - | - | EDL Protection | 2 | - | 90% | DXF_ONLY | Text 'PFR' near EDL inputs.
4 | CONTACTOR | Contactor AC3 | 4P | 250A | - | - | - | - | - | EDL Input Control, ATS-1, ATS-2, ATS-3 Switching | 8 | - | 95% | BOTH | Grouped 2x EDL contactors and 6x ATS contactors (C1/C2). Text 'CONTACTOR', 'C1 4x250A', 'C2 4x250A'.
5 | MCCB | MCCB 250AF | 4P | 200A | C | 36kA | - | - | 150.0 | ATS-1 Main Source Input | 1 | - | 100% | BOTH | Downstream of EDL. Text 'MCCB: AF=250A AT=200A'. Feeds 'FROM EDL' line.
6 | MCCB | MCCB 400AF | 4P | 250A | C | 50kA | - | - | 150.0 | GEN 200kVA | 1 | - | 95% | BOTH | Generator protection. Text 'AF=400A AT=250A'. Cable '4x150mm2'.
7 | MCCB | MCCB 160AF | 4P | 125A | C | 50kA | - | - | - | GEN 100kVA | 1 | - | 95% | BOTH | Generator protection. Text 'AF=160A AT=125A'.
8 | MCCB | MCCB 400AF | 4P | 250A | C | 36kA | - | - | 150.0 | Totalizing Switchboard Outgoing | 1 | - | 95% | BOTH | Main Gen Bus output to ATS-1. Text 'AF=400A AT=250A'.
9 | MCCB | MCCB 160AF | 4P | 150A | C | 36kA | - | - | 70.0 | Generator Subscription | 1 | - | 95% | BOTH | Text 'AF=160A AT=150A'. Cable '4x70mm2'.
10 | MCCB | MCCB 80AF | 4P | 70A | C | 36kA | - | - | 25.0 | Solar | 1 | - | 95% | BOTH | Text 'AF=80A AT=70A'. Cable '4x25mm2'.
11 | SWITCH | Isolator Switch (IS) | 4P | 250A | - | - | - | - | - | ATS Source Isolation | 6 | - | 95% | BOTH | Located at inputs of ATS-1, ATS-2, ATS-3. Text 'IS' and '4x250A'.
12 | SWITCH | Manual Transfer Switch (MTS) | 4P | 250A | - | - | - | - | - | ATS Bypass | 6 | - | 90% | BOTH | Bypass switches for ATS units. Text 'MTS1', 'MTS2' with '4x250A'. Counted as discrete switches per text labels.
13 | SPD | Surge Arrestor | 4P | - | - | - | - | Class B&C | - | ATS-1 Output, ATS-2 Output | 2 | - | 100% | DXF_ONLY | Text 'SURGE ARRESTOR CLASS B&C'.
14 | METER | Digital Power Meter | 4P | - | - | - | - | - | - | ATS-1, ATS-2, ATS-3 Output Analysis | 3 | - | 100% | DXF_ONLY | Text 'DIGITAL POWER METER' at outputs of all 3 ATS units.
15 | OTHER | Phase Relay | - | - | - | - | - | - | 150.0 | Main Output Protection | 1 | ✓ | 90% | DXF_ONLY | Text 'PHASE RELAY' at final output to MDB. Associated cable 4x150mm feeding MDB.

## Terminal Schedule
Terminal Block Schedule · xyz.dwg
Types: 1 ¦ Total terminals: 2
# | Terminal Type | Description | Max mm² | Qty | Circuits
1 | Terminal 70mm²+ | Cable >70mm² — check Phoenix catalog | 70 | 2 | Main Output Protection - @150.0mm²
|  |  | TOTAL | 2

## Enclosure
Panel Enclosure · xyz.dwg
Field | Value
Panel Reference | ATS
Enclosure Size | -
Manufacturer | -
Catalog / Part Number | -

## Additional Info
Additional Information Detected · xyz.dwg
Items detected by AI as extra useful data present in this drawing.
# | Type | Description | Value
1 | TITLE_BLOCK | Project and client details from title block | Project: KORNET EL HAMRA, Client: MRS. JESSICA & MR. PATRICK TOHME, Drawing Title: ATS
2 | NOTE | Cable specifications and types identified in diagram | Power cables (e.g., 4x150mm2+E, 4x35mm2), Control cables (2x6mm2, 4x2.5mm2), CAT6 Data cables
3 | NOTE | System power sources identified | Generators (100kVA, 200kVA), EDL (Utility), Solar PV System
4 | NOTE | Control components mentioned | PLC, Phase Failure Relays (PFR), Contactors, Totalizing Switchboard

## Shop Drawing
Drawing Render · xyz.dwg
Full DXF render from the client's drawing file.

## Summary
Component Summary by Category
Category | Groups | Total Units
CONTACTOR | 1 | 8
MCCB | 7 | 8
METER | 2 | 5
OTHER | 2 | 3
SPD | 1 | 2
SWITCH | 2 | 12